## Hardware and Labling
Hardware Audit Check-List Release Date:: < Date > Ver No:: < X.Y >
Requirement | Audit check points | Status | Reference | Remarks
Occupational Health and Safety
1 | OHS : Adequate lifting equipment/ Tools are in good condition and available as per the specifications/ requirements.
2 | OHS: First aid kit complete and available
3 | OHS: Fire Evacuation Plan
4 | OHS: i. Fire extinguisher maintained (valid date visible) ii. Fire extinguisher easy accessible and free from any obstacle
5 | OHS : Team has copy of the H&S manual, work standards manual, I & C Manuals and Site Specific safety rules
6 | OHS : Trained and qualified personnel are installing and operating the equipment's. |  | Only NSN certified PTID engineers to Lead Site supervision activity.
7 | Standard Installation Guidelines
Important points to be considered during New Node Installation
ØUnpack outside the Switch room
ØNo packing material to be kept inside the switch room
ØAll Spares to be kept in the store room
ØProper color coding to be used for power cabling ; Blue/ Red (-), Black (+)
ØAll nodes to be supplied from 2 different Sources
ØFront/ Back to be aligned
ØNo fire prone material to be inside the switch room
ØNo cardboard box to be kept inside
8 | Cabinet Installation : Cabinets are placed according to the site layout plan (approved) and fixed firmly. Layout plan should indicate rack front/ back and hot/ cold aisle. |  |  | Equipment to be installed facing each other from Front side to Front side
Next row, equipment to be installed facing each other rear side to rear side
9 | Cabinet Installation : All necessary installation accessories are used in correct sequence or order (like expansion bolts with insulation washers, flat washers, spring washers, bolts & nuts) to fix cabinet and base support.
10 | Power & Grounding Cables: Quality of crimped lugs done according to specification
11 | Cabinet Installation : Cabinet/ rack installation should not be on wheels |  |  | Wheel should be removed prior to Installation of cabinet
Cabinet Installation on Rail for DX 200 Platform
12 | Cabinet Installation on False Floor Threaded rod
13 | Power Cable Termination Samples
14 | Cabinet Grounding
15 | Cable Routing inside Cabinet
16 | Cable Routing on Ladder
17 | DDF Cabling and patching
18 | Cabinet Installation : Equipment leveling is proper. The surface of row cabinets is in the same plane and cabinets are arranged in a tight and tidy way & aligned.
19 | Cabinet Installation : No Waste, Dirt or Metallic debris inside or on Equipment and beneath false floor
20 | Cabinet Installation : Door and Lock of cabinet are functioning properly (They should be metallic perforated type, Glass door are not recommended)
21 | Cabinet Installation : Top cover and sides plate installed properly
22 | Cabinet Installation : Labeling of the doors & Safety labels attached
23 | Cabinet Installation : Alarm panel installed according to specifications
24 | Cabinet Installation : Grounding cable connected for cabinet doors & The ESD wrist strap is inserted into the ESD installation hole of the cabinet and used when handling cards
25 | Power & Grounding Cables: Connections done correctly according to specifications
26 | Power & Grounding Cables: Cable routes match those shown on the power layout drawing.
27 | Power & Grounding Cables: Cables labeled correctly
28 | Power & Grounding Cables: AC/ DC cable installed correctly according to specifications
29 | Power & Grounding Cables: No joints in the power/ PGND cables
30 | Cabling: Duct to be used to for routing fiber cables
31 | Power & Grounding Cables: Cable ties installed properly (no sharp or jagged edges)
32 | Signal Cables: No sharp bends in signal cables at Bending points.
33 | Signal Cables: E1 cables are terminated at DDF modules as per specificiations
34 | Signal Cables: Damaged Cabinet/ Equipment not to be Installed
35 | Signal Cables: Unused connectors of the optical patch cords are covered with dust proof caps